Technical Specification for the procurement

of Autonomous Hybrid Power Systems

for the needs of COSCOM LLC

| city | Tashkent |
| --- | --- |
| 2026 |  |

Contents

1.	General Information	2

1.1 Description of Goods (Functional and Consumer Properties)	2

1.2 Purpose of Procurement	2

1.3 Justification for the Project Implementation within which the Procurement is Carried Out	2

1.4 Novelty Information	3

2.	Insurance of Goods	3

3.	General Requirements for the Bidder	3

4.	Technical Specifications of Goods	3

5.	Completeness Requirements	4

6.	Requirements for Maintenance and Operation of Goods	5

7.	Requirements for Operating Costs	5

8.	Requirements for Delivery Time and Place	5

9.	Requirements for Compliance with Technical Regulation Standards	5

10.	Requirements for Supervised Installation	6

11.	Personnel Training Requirements	6

12.	Documentation Requirements	6

13.	Warranty and Post-Warranty Service Requirements	6

14.	Requirements for Remaining Shelf Life, Storage Period and Quality Warranty	6

15.	Additional Requirements	6

16.	List of Abbreviations	6

- General Information

1.1 Description of Goods (Functional and Consumer Properties)

Autonomous Hybrid Power Systems (AHPS) are intended to support radio sites in the complete absence of external power supply and are used for the power supply of the Company's cellular base stations. A framework agreement is expected to be concluded, fixing the unit price and the maximum contract amount, with a validity period of one year.

1.2 Purpose of Procurement

Ensuring uninterrupted and energy-efficient power supply to the facilities of COSCOM LLC with the use of multiple energy sources.

1.3 Justification for the Project Implementation within which the Procurement is Carried Out

Implementation of this project will ensure site availability in the complete absence of mains power supply at the facilities of COSCOM LLC.

1.4 Novelty Information

The supplied autonomous hybrid power systems must be new (goods which have not been used, including not refurbished, with no component parts replaced and no consumer properties restored).

The supplied autonomous hybrid power systems must comply with the requirements of this Technical Specification. The period from the date of manufacture to the date of delivery shall not exceed 1 year.

- Insurance of Goods

No requirements; however, the Supplier shall be liable for the safekeeping of the goods until their official transfer to the Buyer.

- General Requirements for the Bidder

The Supplier shall hold the relevant certificates and permits confirming its right and ability to conduct business activities.

The Supplier shall not be listed in the Unified Register of Unfair Contractors.

The Supplier shall not be involved in any litigation or arbitration proceedings with the Customer.

- Technical Specifications of Goods

The Autonomous Hybrid Power System (AHPS) shall be a complete engineering system, the package of which shall include a diesel generator, batteries (Bat.) and solar panels.

The autonomous hybrid power system shall be designed to operate as the primary power source and shall ensure continuous operation of the facilities of COSCOM LLC 24 hours a day.

Composition of the autonomous hybrid power system:

- Solar panels

- Diesel generator

- Storage batteries LiFePO4

- Battery cabinet with heating and cooling function

- Hybrid inverter with battery charging function

- Charge controller (if not built-in)

- Monitoring and control software

Functional requirements:

- Automatic switching between power sources

- Priority of solar energy use

- Inverter capable of operating in hybrid mode

- Inverter parallel operation support

- Overload and short-circuit protection

- Remote system monitoring and control (mobile application and web interface)

1) Requirements for the 15 kW hybrid system:

Diesel generator specifications:

| Parameters | Specifications |
| --- | --- |
| Rated power, not less than, kW | 16 |
| Rated power, not less than, kVA | 20 |
| Cos φ | 0,8 |
| Alternator type | Synchronous, brushless, with Automatic Voltage Regulator (AVR) |
| Number of phases | 1 or 3 |
| Rotation speed, rpm | 1500 |
| Cooling system | liquid |
| Temperature range | -25+50C |
| Number / arrangement of cylinders | 4 / In-line |
| Cycle | 4-stroke |
| Fuel tank capacity, not less than, L | 500 |
| Coolant heater | yes |
| Fuel tank heater | yes |
| Fuel filter with water separator | yes |
| Voltage, V | 230/400 |
| Frequency, Hz | 50 |
| Charger DC 48V | Yes |
| DGU control supply voltage | 12/24 V |
| Ingress protection rating | IP23 |
| Insulation class | H |
| - Three-phase or single-phase power measurement (Ampere) | Yes |
| - Voltage and current measurement in the generator with display on the control panel | yes |
| - Protection against overload, short circuit, overheating, low oil pressure | yes |
| - Event log, not less than | 250 entries |
| - Engine hour counter | yes |
| - Monitoring system: temperature, pressure, engine speed, fuel level, oil level, voltage, current | yes |
| - Monitoring and control via built-in web server | yes |
| - Wireless / wired Internet connection via GSM/GPRS | yes |
| DGU control via SMS commands | yes |
| Fuel theft protection | yes |
| Check valve in the fuel system | yes |
| Automatic, manual and remote control modes | yes |
| Sound-attenuating enclosure | yes |
| Low-noise mufflers | yes |
| Noise level , dB(A) at a distance of 7 m | Not more than 63 dB(A) |
| Number of start attempts, not less than | Three |
| Warranty period, not less than | 2 years or 2,000 engine hours |
| Spare parts availability, not less than | 5 years |
| Operation manual in Russian or English | yes |

Solar panel specifications:

| Parameters | Specifications |
| --- | --- |
| Panel type | Monocrystalline |
| Number of panels, not less than | 28 pcs |
| Panel rated power, not less than | 550 W |
| Coating | Double glass |
| Efficiency, not less than | 21,5% |
| Ingress protection rating | IP 68 |
| Connectors | MC4 |
| Metal frame | yes |

Battery (Bat.) specifications:

| Parameters | Specifications |
| --- | --- |
| Battery type | LiFePO4 |
| Capacity, not less than | 150 Ah |
| Rated voltage | 48 V |
| Number of batteries | 10 pcs |
| Number of cycles at 80% discharge (at T=25°C), not less than | 5000 |
| Operating temperature (°C): | from 0 to +55 |
| Built-in BMS | Yes |
| Integration with inverter | Yes |
| Overcharge protection | Yes |
| Deep discharge protection | Yes |
| Short-circuit protection | Yes |
| Reverse polarity protection | Yes |
| Temperature protection | Yes |
| Active cell balancing | Yes |
| Thermal cabinet for battery installation with heating and cooling function, ingress protection rating IP65 | Yes |

Hybrid inverter specifications:

| Parameters | Specifications |
| --- | --- |
| Type | Off-grid Hybrid |
| Power, not less than | 15 kW |
| Output | 3×400/230 V |
| Efficiency | ≥96% |
| MPPT | not less than 2 |
| PV input | not less than 18 kW |
| Operation with DGU | Yes |
| Automatic DGU start | Yes |
| Parallel operation | Yes |
| Charge controller | Built-in / External |
| Ingress protection rating | not lower than IP65 |
| Monitoring | Web, SNMP, Modbus |

2) Requirements for the 22 kW hybrid system:

Diesel generator specifications:

| Parameters | Specifications |
| --- | --- |
| Rated power, not less than, kW | 24 |
| Rated power, not less than, kVA | 30 |
| Cos φ | 0,8 |
| Alternator type | Synchronous, brushless, with Automatic Voltage Regulator (AVR) |
| Number of phases | 1 or 3 |
| Rotation speed, rpm | 1500 |
| Cooling system | liquid |
| Temperature range | -25+50C |
| Number / arrangement of cylinders | 4 / In-line |
| Cycle | 4-stroke |
| Fuel tank capacity, not less than, L | 500 |
| Coolant heater | yes |
| Fuel tank heater | yes |
| Fuel filter with water separator | yes |
| Voltage, V | 230/400 |
| Frequency, Hz | 50 |
| Charger DC 48V | Yes |
| DGU control supply voltage | 12/24 V |
| Ingress protection rating | IP23 |
| Insulation class | H |
| - Three-phase or single-phase power measurement (Ampere) | Yes |
| - Voltage and current measurement in the generator with display on the control panel | yes |
| - Protection against overload, short circuit, overheating, low oil pressure | yes |
| - Event log, not less than | 250 entries |
| - Engine hour counter | yes |
| - Monitoring system: temperature, pressure, engine speed, fuel level, oil level, voltage, current | yes |
| - Monitoring and control via built-in web server | yes |
| - Wireless / wired Internet connection via GSM/GPRS | yes |
| DGU control via SMS commands | yes |
| Fuel theft protection | yes |
| Check valve in the fuel system | yes |
| Automatic, manual and remote control modes | yes |
| Sound-attenuating enclosure | yes |
| Low-noise mufflers | yes |
| Noise level , dB(A) at a distance of 7 m | Not more than 63 dB(A) |
| Number of start attempts, not less than | Three |
| Warranty period, not less than | 2 years or 2,000 engine hours |
| Spare parts availability, not less than | 5 years |
| Operation manual in Russian or English | yes |

Solar panel specifications:

| Parameters | Specifications |
| --- | --- |
| Panel type | Monocrystalline |
| Number of panels | 40 pcs |
| Panel rated power, not less than | 550 W |
| Coating | Double glass |
| Efficiency, not less than | 21,5% |
| Ingress protection rating | IP 68 |
| Connectors | MC4 |
| Metal frame | yes |

Battery (Bat.) specifications:

| Parameters | Specifications |
| --- | --- |
| Battery type | LiFePO4 |
| Capacity, not less than | 150 Ah |
| Rated voltage | 48 V |
| Number of batteries | 15 pcs |
| Number of cycles at 80% discharge (at T=25°C), not less than | 5000 |
| Operating temperature (°C): | from 0 to +55 |
| Built-in BMS | Yes |
| Integration with inverter | Yes |
| Overcharge protection | Yes |
| Deep discharge protection | Yes |
| Short-circuit protection | Yes |
| Reverse polarity protection | Yes |
| Temperature protection | Yes |
| Active cell balancing | Yes |
| Thermal cabinet for battery installation with heating and cooling function, ingress protection rating IP65 | Yes |

Hybrid inverter specifications:

| Parameters | Specifications |
| --- | --- |
| Type | Off-grid Hybrid |
| Power, not less than | 22 kW |
| Output | 3×400/230 V |
| Efficiency | ≥96% |
| MPPT | not less than 2 |
| PV input | not less than 25 kW |
| Operation with DGU | Yes |
| Automatic DGU start | Yes |
| Parallel operation | Yes |
| Charge controller | Built-in / External |
| Ingress protection rating | not lower than IP65 |
| Monitoring | Web, SNMP, Modbus |

Quantity of hybrid systems to be supplied:

| Item name | Unit | Qty | Price |
| --- | --- | --- | --- |
| 15 kW hybrid system | pcs | 4 |  |
| 22 kW hybrid system | pcs | 4 |  |
| Monitoring software | Set | 1 |  |

- Completeness Requirements

The quality and completeness of the supplied goods shall comply with the conditions specified in the Specification, the applicable standards and other mandatory requirements of the regulations applicable to this type of products.

- Requirements for Maintenance and Operation of Goods

The materials shall be suitable for operation under the climatic conditions of the Republic of Uzbekistan. All operating materials shall be provided in full in accordance with the technical specifications set out in this Technical Specification (TS).

- Requirements for Operating Costs

No requirements are imposed on the operating costs of the goods.

- Requirements for Delivery Time and Place

The goods shall be delivered to the Customer's warehouse: GSM-1 Technical Warehouse, 2 Temirchi Street, Tashkent. Delivery shall be completed in full configuration no later than 120 calendar days from the date of contract signing.

- Requirements for Compliance with Technical Regulation Standards

The supplied Goods shall comply with the questionnaires (if any), GOST standards, technical conditions (TU), the technical requirements for the Goods, as well as other mandatory requirements applicable to this type of goods established in the Republic of Uzbekistan.

Conformity certificates are mandatory. The Goods shall be certified. The following certificates are required:

- Conformity certificate for a specific or standard type of goods;

- Conformity certificate of the Republic of Uzbekistan — for Goods of foreign origin;

- Hygienic certificate (for Goods subject to mandatory certification);

- Fire safety certificate (for Goods subject to mandatory fire safety certification);

- Quality certificate or another document (form, datasheet, etc.) certifying that the actually supplied Goods comply with the requirements of the Contract (supplied together with the Goods).

- Requirements for Supervised Installation and Commissioning Works

The Supplier shall ensure the performance of supervised installation and commissioning works at the Customer's facilities for the purpose of putting the supplied autonomous hybrid power systems into operation.

As part of the supervised installation and commissioning works, the Supplier shall:

provide technical supervision and control over the installation works;

monitor compliance of the installation with the manufacturer's requirements, technical documentation and applicable regulatory requirements;

verify the correctness of installation and connection of solar panels, storage batteries, hybrid inverters, diesel generator units, protection and switching cabinets, the monitoring system and other equipment included in the supplied system;

configure the equipment, software, charge controllers, battery BMS and the monitoring system;

configure the operating algorithms of the hybrid system, including solar energy priority, battery charging and discharging, and automatic start and stop of the DGU;

carry out comprehensive commissioning works and equipment testing in all operating modes provided for;

verify the operability of the remote monitoring and control system via the web interface and mobile application;

test automatic switching between power sources and the operation of protective mechanisms;

carry out load testing of the equipment;

eliminate any deficiencies related to equipment configuration identified during commissioning works;

prepare and submit to the Customer the acceptance certificates for the completed supervised installation and commissioning works, as well as test reports.

Supervised installation and commissioning works shall be performed by qualified specialists of the Supplier or by an organisation authorised by the manufacturer.

All costs associated with the performance of supervised installation and commissioning works, including transportation costs, travel allowances, accommodation of specialists, necessary tools and software, shall be included in the cost of the supplied equipment.

The equipment shall be deemed put into operation upon successful completion of commissioning works and signing by the Parties of the corresponding commissioning acceptance act.

- Personnel Training Requirements

The Supplier shall conduct training of the Customer's technical personnel in the operation, maintenance and monitoring of the supplied autonomous hybrid power systems.

The training shall be conducted after completion of the supervised installation and commissioning works and prior to signing of the commissioning acceptance act.

As part of the training, the Supplier shall ensure:

familiarisation with the composition and operating principles of the autonomous hybrid power system;

training in the operating rules for solar panels, hybrid inverters, LiFePO4 storage batteries, the diesel generator unit and the monitoring system;

training in the use of the software, web interface and mobile application for remote monitoring and control;

training in the configuration of the main system parameters;

training in personnel actions in the event of emergency and abnormal situations;

training in scheduled maintenance of the equipment;

training in the analysis of event logs, alarm messages and diagnostic information;

provision of operational and training documentation in Russian or English.

The training shall be conducted by qualified specialists of the Supplier or by representatives of the equipment manufacturer.

The number of the Customer's employees to be trained shall be not less than 5 persons.

The duration of the training shall be not less than 1 working day and shall include both theoretical and practical parts directly on the installed equipment.

Upon completion of the training, the Supplier shall provide a training acceptance act and a list of the trained employees.

- Documentation Requirements

Operation manual.

- Warranty and Post-Warranty Service Requirements

The warranty for the goods shall be not less than 2 years. The service life shall be not less than 12 years.

- Requirements for Remaining Shelf Life, Storage Period and Quality Warranty

The Supplier undertakes to ensure that the quality of the goods complies with the required standards and shall be liable to the Buyer for any defects identified in the goods.

- Additional Requirements

No requirements are imposed.

- List of Abbreviations

| No. | Abbreviation | Definition |
| --- | --- | --- |
| 1 | TS | Technical Specification |
| 2 | DGU | Diesel Generator Unit |
| 3 | Bat. | Storage Battery |